Simulation Backend Evaluation

LBNL Modelica Buildings Library vs. AMESim FMU pipeline

Status:  Research / decision support — no code changes
Audience:  Project owner deciding on simulation backend
Date:  8 May 2026

# 1.  Executive summary

The current architecture composes AMESim FMUs into SSP packages and solves them with PyFMI. The concerns driving this review are real: AMESim licensing constrains Celery concurrency by design, runtime license servers are operationally fragile, and the FMU binaries currently in the library are stubs — there is no sunk cost in real AMESim physics yet.

Three viable backends exist. Opinion, not a decision: LBNL's Modelica Buildings Library is the strongest fit because its Experimental.DHC package already contains 5th-generation district heating models that match the project's ambient-loop-with-per-apartment-heat-pumps topology almost one-to-one. The principal risk is OpenModelica's solver maturity for stiff thermo-hydraulic systems; Dymola eliminates that risk but reintroduces a commercial license — without the runtime license-server pattern AMESim uses.

| Dimension | AMESim FMU (current) | LBNL Modelica Buildings | EnergyPlus + OpenStudio |
| --- | --- | --- | --- |
| Licensing cost | High — runtime license server | None (BSD); Dymola optional | None (DOE, public domain) |
| Component fit for ambient loops | Build it yourself | Pre-modelled in Experimental.DHC | Plant loops are rigid; awkward fit |
| Python integration | PyFMI (working today) | BuildingsPy (BSD) | OpenStudio SDK / EnergyPlus API |
| Solver maturity | AMESim mature; PyFMI master OK | Dymola excellent; OpenModelica fair | Mature, but fixed semantics |
| Learning curve from here | Already invested | Modelica + Buildings package | EnergyPlus IDF / OpenStudio model |
| Vendor lock-in | High (AMESim) | None (BSD) or Dymola optional | None |

# 2.  What's already built around FMUs

The FMU coupling is concentrated in a few places. Migration cost depends on which option below is chosen.

| Surface | Path | Notes |
| --- | --- | --- |
| Composition entry | backend/engine/composition.py | CompositionEngine.compose(topology, output_path) |
| Topology → graph | backend/engine/connection_resolver.py | Deepest coupling. Hardcoded port-name patterns at lines 90–91 and 102–103: hydr_out_T, hydr_in_mdot, etc. FMU type strings hardcoded throughout. |
| SSP package | backend/engine/ssp_generator.py | Emits SystemStructure.ssd XML, copies FMU binaries, writes parameter SSV |
| Manifest schema | backend/engine/manifest.py | FMUManifest, PortDefinition, ParameterDefinition |
| Simulation runner | backend/simulation/runner.py | PyFMI Master + Assimulo CVode; calls setup_amesim_environment() for license server |
| Database | backend/app/models/{project,job}.py | ssp_path columns assume the SSP artefact pattern |
| Frontend types | admin/src/types.ts | FMUPort, FMUManifest, FMUTestRunStats |
| FMU catalog | fmu-library/{type}/v1.0.0/*.fmu | All six are stubs from generate_stub_fmus.py |

Honest accounting: the composition pipeline, validator, and SSP packaging are real engineering effort that would be wasted if the FMU paradigm is dropped. The FMU binaries themselves are throwaway stubs — no waste there. Celery dispatch is still a TODO in backend/app/routes/projects.py, so the runtime path has not been hardened against real licensing pressure yet.

# 3.  LBNL Modelica Buildings Library

## What it is

Maintainer: Lawrence Berkeley National Laboratory, repo lbl-srg/modelica-buildings.

Licence: 3-clause BSD (library and BuildingsPy). Commercial use OK; no licence server.

Version: 13.0.0, released 4 May 2026, actively developed.

Top-level packages: Fluid, HeatTransfer, ThermalZones, BoundaryConditions, Controls, Electrical, Airflow, Media, Utilities, Experimental.DHC.

## Why it fits this project specifically

Buildings.Experimental.DHC is the package for district heating and cooling, including 5th-generation networks: ambient-temperature loops (5–35 °C) with per-building Energy Transfer Stations containing water-to-water heat pumps. That is a near-exact match for the project's topology — central heat pump → ambient loop → apartment heat pumps → thermal zones.

Reference component: Buildings.Experimental.DHC.EnergyTransferStations.Combined.Generation5. The Buildings.Experimental.DHC.Examples sub-package contains worked example systems — a starting point for the composition engine to emit, rather than building everything from primitives.

## Tooling around it

Compilers: Dymola (commercial, gold standard for stiff thermo-hydraulic systems), OpenModelica (open source, ~86 % of Buildings models compile cleanly), OPTIMICA (commercial).

Python integration: BuildingsPy (BSD) drives Dymola, OpenModelica and OPTIMICA from Python — runs simulations, parses .mat results, regression tests.

FMI export: All three compilers export FMI 2.0 FMUs. With OpenModelica, --fmuRuntimeDepends=modelica is needed to bundle CVode runtime dependencies into a portable FMU.

# 4.  Component mapping

For every atomic FMU in fmu-library/, an equivalent Buildings model exists. This is what makes a migration tractable rather than a from-scratch rebuild.

| Current FMU type | Buildings library equivalent | Parameter mapping notes |
| --- | --- | --- |
| central_heatpump | Buildings.Fluid.HeatPumps.ScrollWaterToWater or EquationFitWaterToWater | nominal_power_kW → QCon_flow_nominal (W). COP_nominal → performance record. source_type=ground → ground-source ETS variant. |
| apartment_heatpump | Same family at smaller capacity, or DHC.EnergyTransferStations Generation5HeatPump | Same parameter shape as central, smaller QCon_flow_nominal. |
| ambient_loop_segment | Buildings.Fluid.FixedResistances.Pipe or PlugFlowPipe | length_m → length. diameter_mm → dh (m). insulation_thickness_mm → wall-layer record. PlugFlowPipe adds transport-delay and ground heat loss. |
| loop_tee | Buildings.Fluid.FixedResistances.Junction | n_branches constrains topology — Junction is 3-port; multi-way splits become daisy-chained junctions. |
| apartment_thermal_zone | Buildings.ThermalZones.ReducedOrder.RC (ISO 13790) or Detailed.MixedAir | floor_area_m2, ceiling_height_m → geometry. U_wall, U_window, window_area_m2 → envelope. n_occupants → internal-gains. orientation → solar aperture. |
| weather_source | Buildings.BoundaryConditions.WeatherData.ReaderTMY3 | TMY3 .mos files. Location → file selection rather than parameter. |

The shape of a Connection (source/target instance + port) is preserved either way; only port-name conventions change. Buildings uses Modelica's fluid_a/fluid_b connectors, which carry T, mdot and p as a bundle — fewer per-component connections than the current (T, mdot, p) triple-wiring at connection_resolver.py:90-91.

# 5.  Three architectural options

## Option A — Hybrid: keep SSP/PyFMI, swap FMU source

Replace stub AMESim FMUs with FMUs exported from Modelica Buildings models via OpenModelica (or Dymola). Composition engine, runner, SSP pipeline, database schema and frontend types all stay.

Pros. Smallest blast radius. Existing investment in composition + SSP + manifest validation is preserved. Migration is mostly a content swap: new FMU binaries plus new port names and parameter schemas in connection_resolver.py.

Cons. Inherits SSP and FMU-master complexity forever. Two solver layers — PyFMI master coordinating internally CVode-solved Modelica FMUs — is suboptimal numerically vs. a single integrator over the full DAE. Loses access to Modelica's algebraic-solver advantages on stiff coupled systems.

## Option B — Native Modelica: generate .mo from topology JSON

The composition engine emits a Modelica model file using Buildings.Experimental.DHC components; BuildingsPy compiles and runs it. Drop PyFMI, Assimulo, SSP, manifest.py and ssp_generator.py. Results come back as .mat, post-processed to Parquet.

Pros. Single integrator over the full DAE — better numerics for stiff thermo-hydraulic systems with many heat pumps. Smaller surface area: the composition engine becomes a Modelica code generator, no FMU master, no SSP. Direct access to the Buildings library's parameter records and connector bundles.

Cons. Larger refactor: connection_resolver.py, ssp_generator.py, runner.py and manifest.py are reworked or deleted. Database schema: ssp_path becomes model_path or similar. Frontend types lose FMUPort / FMUManifest shape. The current port-introspection UX in FMULibrary.tsx needs a Modelica-aware equivalent.

## Option C — EnergyPlus + OpenStudio SDK (different paradigm)

EnergyPlus is mature, free (DOE) and battle-tested for whole-building energy simulation. The OpenStudio SDK provides a Ruby/C++/Python API to build and run models.

Decisive con. EnergyPlus's plant-loop topology is rigid — ambient-loop networks with novel branching are awkward to express. Per-apartment heat pumps drawing from a shared ambient loop is closer to what the Modelica DHC package was built for. EnergyPlus would force the topology into a shape this project has explicitly tried to avoid. Included for completeness; not a serious contender here.

# 6.  Risks and unknowns

OpenModelica compatibility cliff. The 14 % of Buildings models that fail to compile under OpenModelica have not been audited for this project's needs. Concretely: do Buildings.Experimental.DHC.EnergyTransferStations.Combined.Generation5* and Buildings.Fluid.HeatPumps.ScrollWaterToWater compile cleanly? Unknown until tested.

Solver convergence on year-long simulations. A building with 30+ apartment heat pumps each with their own controller is a stiff system. Dymola handles this routinely; OpenModelica's CVode integration may need tolerance tuning, event-handling adjustments, or fall over entirely on some configurations.

Dymola fallback economics. If OpenModelica proves unreliable, Dymola is roughly €5–15 k per seat — significantly cheaper than AMESim and licensed per-seat (no runtime license server). Trades open source for reliability while still removing the operational pain point.

Frontend re-modelling. Option B forces the FMU-aware types and components in admin/src/pages/FMULibrary.tsx to be reconceived. Not a blocker, but real UI work.

Data-file injection coupling. The runner's AMESim .data file injection becomes irrelevant in either A or B — code to delete, not migrate.

# 7.  Suggested next step

Before committing to A or B, run a time-boxed spike of 1–2 days answering one question: does a 5GDHC example from Buildings.Experimental.DHC.Examples compile under OpenModelica and run a year-long simulation reliably from BuildingsPy?

Concrete spike steps:

Install OpenModelica plus the Buildings library locally.

Pick the closest example to this project's topology — a single ambient loop, multiple buildings or apartments with heat pumps.

Drive it from BuildingsPy: compile, run for 31 536 000 s with 900 s step, dump .mat, parse to a DataFrame.

Note compile time, simulation wall-clock, peak memory, and any solver failures or warnings.

If the spike passes, Option B becomes the recommendation. If it fails on Buildings library models specifically (rather than on local setup), Option A becomes a safer bet, or Dymola enters the picture.

# Sources

LBNL Modelica overview & BuildingsPy: https://simulationresearch.lbl.gov/modelica/

Repo, releases, BSD license: https://github.com/lbl-srg/modelica-buildings

5GDHC examples roadmap: https://github.com/lbl-srg/modelica-buildings/issues/1769

Generation 5 ETS reference: https://simulationresearch.lbl.gov/modelica/releases/v8.0.0/help/Buildings_Experimental_DHC_EnergyTransferStations_Combined_Generation5.html

DOE peer review on Spawn + MBL: https://www.energy.gov/sites/default/files/2024-11/bto-peer-2024-35511-35512-35517-35527-spawn-modelica-bldgs-library-wetter.pdf

OpenModelica FMI export guide: https://openmodelica.org/doc/OpenModelicaUsersGuide/latest/fmitlm.html